## Sheet1
Tamil Nadu Fire and Rescue Services
Requirement of the Fire Safety measures for varies categories – Above 15 m in height
Group A - Residential Building
Sl.No | Type of Fire Protection Required | A3- Dormitories, A4- Apartments Houses |  |  |  | A5- Hotels
| Fire Safety (Active Measures) | 15 Mts not exceeding 35 Mts | 35 Mts not exceeding 45 Mts | 45 Mts not exceeding 60 Mts | Above 60 Mts | 15 Mts not exceeding 30 Mts | Above 30 Mts and A6 Hotels (Starred)
a | b | c | d | e | f | g | h
1 | Fire Extinguishers | Minimum 2 per floor Depending upon the Area and Travel Distance | Minimum 2 per floor Depending upon the Area and Travel Distance | Minimum 2 per floor Depending upon the Area and Travel Distance | Minimum 2 per floor Depending upon the Area and Travel Distance | Minimum 2 per floor Depending upon the Area and Travel Distance | Minimum 2 per floor Depending upon the Area and Travel Distance
2 | Terrace Level Over Head Tank | 25,000 litres capacity | 5,000 litres (5,000 litres if basement) | 10,000 litres capacity | 25,000 litres capacity | 20,000 litres capacity | 20,000 litres capacity
3 | Under Ground Water Tank | Not Required | 75,000 litres capacity | 75,000 litres capacity | 1,00,000 litres capacity | 1,50,000 litres capacity | 2,00,000 litres capacity
4 | Terrace Fire Pump | 900 LPM at Terrace level Tank | Not Required | Not Required | Not Required | Not Required | Not Required
5 | Fire Pump near Under Group Water Tank | Not Required | 1 electric pump & 1 Diesel pump of capacity 1620 LPM & Jockey Pump 180 LPM | 1 electric pump & 1 Diesel pump of capacity 2280 LPM & Jockey Pump 180 LPM | 2 electric pump & 1 Diesel pump of capacity 2280 LPM & Jockey Pump 180 LPM | 1 electric pump & 1 Diesel pump of capacity 2280LPM & Jockey Pump 180 LPM | 2 electric pump & 1 Diesel pump of capacity 2850 LPM & Jockey Pump 180 LPM
6 | Hose Reel Assembly | Required | Required | Required | Required | Required | Required
7 | Down Comer System | Required | Not Required | Not Required | Not Required | Not Required | Not Required
8 | Wet Riser System | Not Required | Required | Required | Required | Required | Required
9 | Yard Hydrant | Not Required | Not Required | Required | Required | Required | Required
10 | Fire Service Inlet | Required | Required | Required | Required | Required | Required
11 | Manually Operated Fire Alarm Call Point (MCP) | Required | Required | Required | Required | Required | Required
12 | Automatic Detection & Alarm System | Not Required | Not Required | Not Required | Required | Required | Required
13 | Automatic Sprinkler System | Required if area of basement exceeds 200 Sq.mts | Required if area of basement exceeds 200 Sq.mts | Required | Required | Required | Required
a | b |  | c | d | e | f | g | h
Life Safety (passive measure)
14 | Side Set Back Area |  | As per DCR and Local Body Rules | As per DCR and Local Body Rules | As per DCR and Local Body Rules | As per DCR and Local Body Rules | As per DCR and Local Body Rules | As per DCR and Local Body Rules
15 | Parking Facility |  | Required | Required | Required | Required | Required | Required
16 | Assembly Point |  | Required | Required | Required | Required | Required | Required
17 | Compartmentation |  | Required | Required | Required | Required | Required | Required
18 |  | Escape | Required | Required | Required | Required | Required | Required
| Means of | Exit with | 1.5 Mts | 1.5 Mts | 1.5 Mts | 1.5 Mts | 1.5 Mts | 1.5 Mts
|  | Travel Distance , etc | 30 s | 30 Mts | 30 Mts | 30 Mts | 30 Mts | 30 Mts
19 | Staircases |  | Required | Required | Required | Required | Required | Required
20 | Ramp |  | Required if basement | Required if basement | Required if basement | Required if basement | Required if basement | Required if basement
21 | Refuge Area |  | Required at 24th Mts level | Required at 24th Mts level & every 15th Mtrs level | Required at 24th Mts level & every 15th Mtrs level | Required at 24th Mts level & every 15th Mtrs level | Required at 24th Mts level & every 15th Mtrs level | Required at 24th Mts level & every 15th Mtrs level
22 | Exit Signage’s |  | Required | Required | Required | Required | Required | Required
23 | Sealing of Cable and other ducts at each floor level |  | Required | Required | Required | Required | Required | Required
24 | Fire Damper at Air Conditioned Ducts |  | Required | Required | Required | Required | Required | Required
25 | Fire Drill and Fire Order |  | Required | Required | Required | Required | Required | Required
26 | Do’s and Don’ts Laminated Hanging Pads |  | Required | Required | Required | Required | Required | Required
27 | Lighting Arrester |  | Required | Required | Required | Required | Required | Required
28 | Smoke Ventilation System |  | Required | Required | Required | Required | Required | Required
29 | Training |  | Required | Required | Required | Required | Required | Required
30 | House Keeping |  | Required | Required | Required | Required | Required | Required
31 | Emergency Lights (at Staircase Landing and Exit Route |  | Required | Required | Required | Required | Required | Required
32 | Fire Lift |  | Required | Required | Required | Required | Required | Required
Tamil Nadu Fire and Rescue Services
Requirement of the Fire Safety measures for varies categories – Above 15 m in height
Group C - Institutional Building
Sl.No | Type of Fire Protection Required | C1- Hospitals, Sanatoria and Nursing Home |  | C2 - Custodial Institutions
C3 - Penal and Mental Institutions
| Fire Safety (Active Measures) | 15 Mts not exceeding | 24 Mts not exceeding | 15 Mts not exceeding | 24 Mts not exceeding
|  | 24 Mts | 30 Mts | 24 Mts | 30 Mts
a | b | c | d | e | f
1 | Fire Extinguishers | Minimum 2 per floor Depending upon the Area and Travel Distance | Minimum 2 per floor Depending upon the Area and Travel Distance | Minimum 2 per floor Depending upon the Area and Travel Distance | Minimum 2 per floor Depending upon the Area and Travel Distance
2 | Terrace Level Over Head Tank | 20,000 litres capacity | 20,000 litres capacity | 10,000 litres capacity | 20,000 litres capacity
3 | Under Ground Water Tank | 1.00,000 litres capacity | 1,50,000 litres capacity | 75,000 litres capacity | 1,00,000 litres capacity
4 | Terrace Fire Pump | Not required | Not Required | Not Required | Not Required
5 | Fire Pump near Under Group Water Tank | 1 electric pump & 1 Diesel pump of capacity 2280 LPM & Jockey Pump 180 LPM | 2 electric pump & 1 Diesel pump of capacity 2280 LPM & Jockey Pump 180 LPM | 1 electric pump & 1 Diesel pump of capacity 2280 LPM & Jockey Pump 180 LPM | 2 electric pump & 1 Diesel pump of capacity 2850 LPM & Jockey Pump 180 LPM
6 | Hose Reel Assembly | Required | Required | Required | Required
7 | Down Comer System | Not Required | Not Required | Not Required | Not Required
8 | Wet Riser System | Required | Required | Required | Required
9 | Yard Hydrant | Required | Required | Required | Required
10 | Fire Service Inlet | Required | Required | Required | Required
11 | Manually Operated Fire Alarm Call Point (MCP) | Required | Required | Required | Required
12 | Automatic Detection & Alarm System | Required | Required | Required | Required
13 | Automatic Sprinkler System | Required | Required | Required | Required
a | b |  | c | d | e | f
Life Safety (passive measure)
14 | Side Set Back Area |  | As per DCR and Local Body Rules | As per DCR and Local Body Rules | As per DCR and Local Body Rules | As per DCR and Local Body Rules
15 | Parking Facility |  | Required | Required | Required | Required
16 | Assembly Point |  | Required | Required | Required | Required
17 | Compartmentation |  | Required | Required | Required | Required
18 |  | Escape | Required | Required | Required | Required
| Means of | Exit with | 2 Mts | 2 Mts | 2 Mts | 2 Mts
|  | Travel Distance , etc | 30 Mts | 30 Mts | 30 Mts | 30 Mts
19 | Staircases |  | Required | Required | Required | Required
20 | Ramp |  | Required | Required | Required | Required
21 | Refuge Area |  | Required at every floor level | Required at every floor level | Required at every floor level | Required at every floor level
22 | Exit Signage’s |  | Required | Required | Required | Required
23 | Sealing of Cable and other ducts at each floor level |  | Required | Required | Required | Required
24 | Fire Damper at Air Conditioned Ducts |  | Required | Required | Required | Required
25 | Fire Drill and Fire Order |  | Required | Required | Required | Required
26 | Do’s and Don’ts Laminated Hanging Pads |  | Required | Required | Required | Required
27 | Lighting Arrester |  | Required | Required | Required | Required
28 | Smoke Ventilation System |  | Required | Required | Required | Required
29 | Training |  | Required | Required | Required | Required
30 | House Keeping |  | Required | Required | Required | Required
31 | Emergency Lights (at Staircase Landing and Exit Route |  | Required | Required | Required | Required
32 | Fire Lift |  | Required | Required | Required | Required
33 | Ambulance |  | Required | Required | Required | Required
34 | Separate toilet |  | Required specially designed for physically challenged patients | Required | Required | Required
Tamil Nadu Fire and Rescue Services
Requirement of the Fire Safety measures for varies categories – Above 15 m in height
Group D - Assembly Building
Sl.No | Type of Fire Protection Required | D1 - Theartre over 1000 persons, D2 upto 1000 persons D3 - Permanent Stage over 300 persons |  | D6 - Not exceeding 30 mtrs | D7 - Elevated or underground for assembly not covered D1-D6
D4 - upto 300 persons, D5 all others
| Fire Safety (Active Measures) | 15 Mts not exceeding | 24 Mts not exceeding | 15 Mts not exceeding | 24 Mts not exceeding
|  | 24 Mts | 30 Mts | 24 Mts | 30 Mts
a | b | c | d | e | f
1 | Fire Extinguishers | Minimum 2 per floor Depending upon the Area and Travel Distance | Minimum 2 per floor Depending upon the Area and Travel Distance | Minimum 2 per floor Depending upon the Area and Travel Distance | Minimum 2 per floor Depending upon the Area and Travel Distance
2 | Terrace Level Over Head Tank | 10,000 litres capacity | 20,000 litres capacity | 20,000 litres capacity | 20,000 litres capacity
3 | Under Ground Water Tank | 75,000 litres capacity | 1,00,000 litres capacity | 1,00,000 litres capacity | 1,00,000 litres capacity
D1-D5, 2,00,000 litres for D6 Multiplex
4 | Terrace Fire Pump | Not required | Not Required | Not Required | Not Required
5 | Fire Pump near Under Group Water Tank | 1 electric pump & 1 Diesel pump of capacity 2280 LPM & Jockey Pump 180 LPM | 2 electric pump & 1 Diesel pump of capacity 2280 LPM & Jockey Pump 180 LPM | 2 electric pump & 1 Diesel pump of capacity 2850 LPM & Jockey Pump 180 LPM | 2 electric pump & 1 Diesel pump of capacity 2850 LPM & Jockey Pump 180 LPM
6 | Hose Reel Assembly | Required | Required | Required | Required
7 | Down Comer System | Not Required | Not Required | Not Required | Not Required
8 | Wet Riser System | Required | Required | Required | Required
9 | Yard Hydrant | Required | Required | Required | Required
10 | Fire Service Inlet | Required | Required | Required | Required
11 | Manually Operated Fire Alarm Call Point (MCP) | Required | Required | Required | Required
12 | Automatic Detection & Alarm System | Required | Required | Required | Required
13 | Automatic Sprinkler System | Required | Required | Required | Required
a | b |  | c | d | e | f
Life Safety (passive measure)
14 | Side Set Back Area |  | As per DCR and Local Body Rules | As per DCR and Local Body Rules | As per DCR and Local Body Rules | As per DCR and Local Body Rules
15 | Parking Facility |  | Required | Required | Required | Required
16 | Assembly Point |  | Required | Required | Required | Required
17 | Compartmentation |  | Required | Required | Required | Required
18 |  | Escape | Required | Required | Required | Required
| Means of | Exit with | 2 Mts | 2 Mts | 2 Mts | 2 Mts
|  | Travel Distance , etc | 30 Mts | 30 Mts | 30 Mts | 30 Mts
19 | Staircases |  | Required | Required | Required | Required
20 | Ramp |  | Required If basement floor | Required If basement floor | Required If basement floor | Required If basement floor
21 | Refuge Area |  | Not Required | Required at 24th mtrs level | Required at 24th mtrs level | Required at 24th mtrs level
22 | Exit Signage’s |  | Required | Required | Required | Required
23 | Sealing of Cable and other ducts at each floor level |  | Required | Required | Required | Required
24 | Fire Damper at Air Conditioned Ducts |  | Required | Required | Required | Required
25 | Fire Drill and Fire Order |  | Required | Required | Required | Required
26 | Do’s and Don’ts Laminated Hanging Pads |  | Required | Required | Required | Required
27 | Lighting Arrester |  | Required | Required | Required | Required
28 | Smoke Ventilation System |  | Required | Required | Required | Required
29 | Training |  | Required | Required | Required | Required
30 | House Keeping |  | Required | Required | Required | Required
31 | Emergency Lights (at Staircase Landing and Exit Route |  | Required | Required | Required | Required
32 | Fire Lift |  | Required | Required | Required | Required
Tamil Nadu Fire and Rescue Services
Requirement of the Fire Safety measures for varies categories – Above 15 m in height
Group E - Business Building
Sl.No | Type of Fire Protection Required | E1 offices, banks, professional establishments, like offices of architects, engineers, doctors, lawyers and police stations, E2 - Laboratories research establishments, libraries and test houses. E3 - Computer installations, E4 - Telephone Exchanges, E5 - Broadcasting stations and T.V. stations
| Fire Safety (Active Measures) | 15 Mts not exceeding | 24 Mts not exceeding | Above 30 mtr
|  | 24 Mts | 30 Mts
a | b | c | d | e
1 | Fire Extinguishers | Minimum 2 per floor Depending upon the Area and Travel Distance | Minimum 2 per floor Depending upon the Area and Travel Distance | Minimum 2 per floor Depending upon the Area and Travel Distance
2 | Terrace Level Over Head Tank | 10,000 litres capacity | 20,000 litres capacity | 20,000 litres capacity
3 | Under Ground Water Tank | 75,000 litres capacity | 1,00,000 litres capacity | 2,00,000 litres capacity
4 | Terrace Fire Pump | Not required | Not Required | Not Required
5 | Fire Pump near Under Group Water Tank | 1 electric pump & 1 Diesel pump of capacity 2280 LPM & Jockey Pump 180 LPM | 2 electric pump & 1 Diesel pump of capacity 2280 LPM & Jockey Pump 180 LPM | 2 electric pump & 1 Diesel pump of capacity 2850 LPM & Jockey Pump 180 LPM
6 | Hose Reel Assembly | Required | Required | Required
7 | Down Comer System | Not Required | Not Required | Not Required
8 | Wet Riser System | Required | Required | Required
9 | Yard Hydrant | Required | Required | Required
10 | Fire Service Inlet | Required | Required | Required
11 | Manually Operated Fire Alarm Call Point (MCP) | Required | Required | Required
12 | Automatic Detection & Alarm System | Required | Required | Required
13 | Automatic Sprinkler System | Required | Required | Required
a | b |  | c | d | e
Life Safety (passive measure)
14 | Side Set Back Area |  | As per DCR and Local Body Rules | As per DCR and Local Body Rules | As per DCR and Local Body Rules
15 | Parking Facility |  | Required | Required | Required
16 | Assembly Point |  | Required | Required | Required
17 | Compartmentation |  | Required | Required | Required
18 |  | Escape | Required | Required | Required
| Means of | Exit with | 2 Mts | 2 Mts | 2 Mts
|  | Travel Distance , etc | 30 Mts | 30 Mts | 30 Mts
19 | Staircases |  | Required | Required | Required
20 | Ramp |  | Required If basement floor | Required If basement floor | Required If basement floor
21 | Refuge Area |  | Not Required | Required at 24th mtrs level | Required at 24th mtrs level and every 15 mtrs level one.
22 | Exit Signage’s |  | Required | Required | Required
23 | Sealing of Cable and other ducts at each floor level |  | Required | Required | Required
24 | Fire Damper at Air Conditioned Ducts |  | Required | Required | Required
25 | Fire Drill and Fire Order |  | Required | Required | Required
26 | Do’s and Don’ts Laminated Hanging Pads |  | Required | Required | Required
27 | Lighting Arrester |  | Required | Required | Required
28 | Smoke Ventilation System |  | Required | Required | Required
29 | Training |  | Required | Required | Required
30 | House Keeping |  | Required | Required | Required
31 | Emergency Lights (at Staircase Landing and Exit Route |  | Required | Required | Required
32 | Fire Lift |  | Required | Required | Required
Tamil Nadu Fire and Rescue Services
Requirement of the Fire Safety measures for varies categories – Above 15 m in height
Group F - Mercantile Building
Sl.No | Type of Fire Protection Required | F1 - Shops, Stores upto 500 Sq.m, |  | F3 - Under ground shopping centre and Storage
F2 - Shops, Stores more than 500 Sq.mtrs.
| Fire Safety (Active Measures) | 15 Mts not exceeding | 24 Mts not exceeding
|  | 24 Mts | 30 Mts
a | b | c | d | e
1 | Fire Extinguishers | Minimum 2 per floor Depending upon the Area and Travel Distance | Minimum 2 per floor Depending upon the Area and Travel Distance | Minimum 2 per floor Depending upon the Area and Travel Distance
2 | Terrace Level Over Head Tank | 10,000 litres capacity | 10,000 litres capacity | 10,000 litres capacity
3 | Under Ground Water Tank | 1,00,000 litres capacity | 1,50,000 litres capacity | 1,50,000 litres capacity
4 | Terrace Fire Pump | Not required | Not Required | Not Required
5 | Fire Pump near Under Group Water Tank | 2 electric pump & 1 Diesel pump of capacity 2280 LPM & Jockey Pump 180 LPM | 2 electric pump & 1 Diesel pump of capacity 2280 LPM & Jockey Pump 180 LPM | 2 electric pump & 1 Diesel pump of capacity 2280 LPM & Jockey Pump 180 LPM
6 | Hose Reel Assembly | Required | Required | Required
7 | Down Comer System | Not Required | Not Required | Not Required
8 | Wet Riser System | Required | Required | Required
9 | Yard Hydrant | Required | Required | Required
10 | Fire Service Inlet | Required | Required | Required
11 | Manually Operated Fire Alarm Call Point (MCP) | Required | Required | Required
12 | Automatic Detection & Alarm System | Required | Required | Required
13 | Automatic Sprinkler System | Required | Required | Required
a | b |  | c | d | e
Life Safety (passive measure)
14 | Side Set Back Area |  | As per DCR and Local Body Rules | As per DCR and Local Body Rules | As per DCR and Local Body Rules
15 | Parking Facility |  | Required | Required | Required
16 | Assembly Point |  | Required | Required | Required
17 | Compartmentation |  | Required | Required | Required
18 |  | Escape | Required | Required | Required
| Means of | Exit with | 1.5 Mts | 1.5Mts | 1.5 Mts
|  | Travel Distance , etc | 30 Mts | 30 Mts | 30 Mts
19 | Staircases |  | Required | Required | Required
20 | Ramp |  | Required If basement floor | Required If basement floor | Required If basement floor
21 | Refuge Area |  | Not Required | Required at 24th mtrs level | Not Required
22 | Exit Signage’s |  | Required | Required | Required
23 | Sealing of Cable and other ducts at each floor level |  | Required | Required | Required
24 | Fire Damper at Air Conditioned Ducts |  | Required | Required | Required
25 | Fire Drill and Fire Order |  | Required | Required | Required
26 | Do’s and Don’ts Laminated Hanging Pads |  | Required | Required | Required
27 | Lighting Arrester |  | Required | Required | Required
28 | Smoke Ventilation System |  | Required | Required | Required
29 | Training |  | Required | Required | Required
30 | House Keeping |  | Required | Required | Required
31 | Emergency Lights (at Staircase Landing and Exit Route |  | Required | Required | Required
32 | Fire Lift |  | Required | Required | Required
Tamil Nadu Fire and Rescue Services
Requirement of the Fire Safety measures for varies categories – Above 15 m in height not to be permitted 18 litres in height
Group G - Industrial Building
Sl. | Type of Fire Protection Required |  | G1 - Low Hazard Industries |  |  |  | G2 - Moderate Hazard Industries
No | Fire Safety (Active Measures) |  | Built up area upto 100 Sq.mt | Built up area more than 100 Sq.mt. & upto 500 Sq.mt | More than 500 Sq.mtrs |  | Built up are upto 100Sq.mtrs | Built up are more than 100Sq.mtrs and upto 500 Sq.mtrs |  | Built up are more than 500Sq.mtrs and upto 1000 Sq.mtrs | Built up area upto 1000 Sq.mt
a | b |  | c | d |  | e | f | g | h |  | i
1 | Fire Extinguishers |  | Minimum 2 per floor Depending upon the Area and Travel Distance | Minimum 2 per floor Depending upon the Area and Travel Distance |  | Minimum 2 per floor Depending upon the Area and Travel Distance | Minimum 2 per floor Depending upon the Area and Travel Distance | Minimum 2 per floor Depending upon the Area and Travel Distance | Minimum 2 per floor Depending upon the Area and Travel Distance |  | Minimum 2 per floor Depending upon the Area and Travel Distance
Ù. | Terrace Level Over Head Tank |  | 5000 litres in case of basement area exceeds 200m2 | 5000 litres add 5000 litres if the provision of sprinkler in basement |  | 10,000 litres capacity | 10,000 Liters capacity | 10,000 Liters capacity | 20,000 Litres capacity |  | 20,000 Litres capacity
3 | Under Ground Water Tank |  | Not required | Not required |  | 1,00,000 litres | Not required | Not required | 75,000 Litres capacity |  | 1,00,000 Litres capacity
4 | Terrace Fire Pump |  | 450 LPM | 450 LPM |  | 450 LPM | 900 LPM | 900 LPM | 900 LPM |  | 900 LPM
5 | Fire Pump near Under Group Water Tank |  | Not required | Not required |  | 1 electric pump & 1 Diesel pump of capacity 2280 LPM & Jockey Pump 180 LPM | Not required | Not required | 1 electric pump & 1 Diesel pump of capacity 2280 LPM & Jockey Pump 180 LPM |  | 1 electric pump & 1 Diesel pump of capacity 2280 LPM & Jockey Pump 180 LPM
6 | Hose Reel Assembly |  | Not required | Required |  | Required | Required | Required | Required |  | Required
7 | Down Comer System |  | Not required | Required |  | Required | Not required | Not required | Required |  | Required
8 | Wet Riser System |  | Not required | Not required |  | Required | Not Required | Not Required | Required |  | Required
9 | Yard Hydrant |  | Not required | Not required |  | Required | Not Required | Not Required | Required |  | Required
10 | Fire Service Inlet |  | Not required | Not required |  | Required | Not Required | Not Required | Required |  | Required
11 | Manually Operated Fire Alarm Call Point (MCP) |  | Not required | Not required |  | Not Required | Not Required | Not Required | Required |  | Required
12 | Automatic Detection & Alarm System |  | Not required | Not required |  | Required | Not Required | Not Required | Required |  | Required
13 | Automatic Sprinkler System |  | Required | Required |  | Required | Required | Required | Required |  | Required
|  |  | (if basement) | (if basement)
Life Safety (passive measure)
14 | Side Set Back Area |  | As per DCR and Local Body Rules | As per DCR and Local Body Rules |  | As per DCR and Local Body Rules | As per DCR and Local Body Rules | As per DCR and Local Body Rules | As per DCR and Local Body Rules |  | As per DCR and Local Body Rules
15 | Parking Facility |  | Required | Required |  | Required | Required | Required | Required |  | Required
16 | Assembly Point |  | Required | Required |  | Required | Required | Required | Required |  | Required
17 | Compartmentation |  | Required | Required |  | Required | Required | Required | Required |  | Required
18 |  | Escape | Required | Required |  | Required | Required | Required | Required |  | Required
| Means of | Exit with | 1.5 Mtrs | 1.5 Mtrs |  | 1.5 Mtrs | 1.5 Mtrs | 1.5 Mtrs | 1.5 Mtrs |  | 1.5 Mtrs
|  | Travel Distance , etc | 45 Mtrs | 45 Mtrs |  | 45 Mtrs | 45 Mtrs | 45 Mtrs | 45 Mtrs |  | 45 Mtrs
19 | Staircases |  | Required | Required |  | Required | Required | Required | Required |  | Required
20 | Ramp |  | Not required | Not required |  | Not required | Not required | Not required | Not required |  | Not required
21 | Refuge Area |  | Not required | Not required |  | Not required | Not required | Not required | Not required |  | Not required
22 | Exit Signage’s |  | Required | Required |  | Required | Required | Required | Required |  | Required
23 | Sealing of Cable and other ducts at each floor level |  | Required | Required |  | Required | Required | Required | Required |  | Required
24 | Fire Damper at Air Conditioned Ducts |  | Required | Required |  | Required | Required | Required | Required |  | Required
25 | Fire Drill and Fire Order |  | Required | Required |  | Required | Required | Required | Required |  | Required
26 | Do’s and Don’ts Laminated Hanging Pads |  | Required | Required |  | Required | Required | Required | Required |  | Required
27 | Lighting Arrester |  | Required | Required |  | Required | Required | Required | Required |  | Required
28 | Smoke Ventilation System |  | Required | Required |  | Required | Required | Required | Required |  | Required
29 | Training |  | Required | Required |  | Required | Required | Required | Required |  | Required
30 | House Keeping |  | Required | Required |  | Required | Required | Required | Required |  | Required
31 | Emergency Lights (at Staircase Landing and Exit Route |  | Required | Required |  | Required | Required | Required | Required |  | Required

## Group A
Requirement of the Fire Safety measures for Group A - Residential Buildings – Above 15 m in height
Sl. No | Type of Fire Protection Required | A3- Dormitories, A4- Apartments Houses |  |  |  | A5- Hotels
| Fire Safety (Active Measures) | 15 Mts not exceeding 35 Mts | 35 Mts not exceeding 45 Mts | 45 Mts not exceeding 60 Mts | Above 60 Mts | 15 Mts not exceeding 30 Mts | Above 30 Mts and A6 Hotels (Starred)
a | b | c | d | e | f | g | h
1 | Fire Extinguishers | Minimum 2 per floor Depending upon the Area and Travel Distance
2 | Terrace Level Over Head Tank | 25,000 litres capacity | 5,000 litres (5,000 litres if basement) | 10,000 litres capacity | 25,000 litres capacity | 20,000 litres capacity | 20,000 litres capacity
3 | Under Ground Water Tank | Not Required | 75,000 litres capacity | 75,000 litres capacity | 1,00,000 litres capacity | 1,50,000 litres capacity | 2,00,000 litres capacity
4 | Terrace Fire Pump | 900 LPM at Terrace level Tank | Not Required | Not Required | Not Required | Not Required | Not Required
5 | Fire Pump near Under Group Water Tank | Not Required | 1 electric pump & 1 Diesel pump of capacity 1620 LPM & Jockey Pump 180 LPM | 1 electric pump & 1 Diesel pump of capacity 2280 LPM & Jockey Pump 180 LPM | 2 electric pump & 1 Diesel pump of capacity 2280 LPM & Jockey Pump 180 LPM | 1 electric pump & 1 Diesel pump of capacity 2280LPM & Jockey Pump 180 LPM | 2 electric pump & 1 Diesel pump of capacity 2850 LPM & Jockey Pump 180 LPM
6 | Hose Reel Assembly | Required | Required | Required | Required | Required | Required
7 | Down Comer System | Required | Not Required | Not Required | Not Required | Not Required | Not Required
8 | Wet Riser System | Not Required | Required | Required | Required | Required | Required
9 | Yard Hydrant | Not Required | Not Required | Required | Required | Required | Required
10 | Fire Service Inlet | Required | Required | Required | Required | Required | Required
11 | Manually Operated Fire Alarm Call Point (MCP) | Required | Required | Required | Required | Required | Required
12 | Automatic Detection & Alarm System | Not Required | Not Required | Not Required | Required | Required | Required
13 | Automatic Sprinkler System | Required if area of basement exceeds 200 Sq.mts | Required if area of basement exceeds 200 Sq.mts | Required | Required | Required | Required
a | b | c | d | e | f | g | h
Life Safety (passive measure)
14 | Side Set Back Area | As per DCR and Local Body Rules | As per DCR and Local Body Rules | As per DCR and Local Body Rules | As per DCR and Local Body Rules | As per DCR and Local Body Rules | As per DCR and Local Body Rules
15 | Parking Facility | Required | Required | Required | Required | Required | Required
16 | Assembly Point | Required | Required | Required | Required | Required | Required
17 | Compartmentation | Required | Required | Required | Required | Required | Required
18 | Means of Escape | Required | Required | Required | Required | Required | Required
| Exit width | 1.5 Mts | 1.5 Mts | 1.5 Mts | 1.5 Mts | 1.5 Mts | 1.5 Mts
| Travel Distance etc. | 30 s | 30 Mts | 30 Mts | 30 Mts | 30 Mts | 30 Mts
19 | Staircases | Minimum of 2 Nos. Location should not be adjacent and should be away from each other.( remote from each other)
20 | Ramp | Required if basement | Required if basement | Required if basement | Required if basement | Required if basement | Required if basement
21 | Refuge Area | Required at 24th Mts level, if there is no balcony | Required at 24th metre and at every 15th Mtr level, if there is no balcony
22 | Exit Signage’s | Required | Required | Required | Required | Required | Required
23 | Sealing of Cable and other ducts at each floor level | Required | Required | Required | Required | Required | Required
24 | Fire Damper at Air Conditioned Ducts | Required | Required | Required | Required | Required | Required
25 | Fire Drill and Fire Order | Required | Required | Required | Required | Required | Required
26 | Do’s and Don’ts Laminated Hanging Pads | Required | Required | Required | Required | Required | Required
27 | Lightning Arrester | Required | Required | Required | Required | Required | Required
28 | Smoke Ventilation System | Required | Required | Required | Required | Required | Required
29 | Training | Required | Required | Required | Required | Required | Required
30 | House Keeping | Required | Required | Required | Required | Required | Required
31 | Emergency Lights (at Staircase Landing and Exit Route | Required | Required | Required | Required | Required | Required
32 | Fire Lift | Required | Required | Required | Required | Required | Required

## Group B
Requirements of Fire Safety measures for Group B - Educational Buildings of above 15 mts in height
Sl.No | Type of Fire Protection Required |  | B-1 Schools up to Senior Secondary Level B-2 All others/training Institutions Ground + One Storey
Fire Safety (Active Measures)
a | b |  | c
1 | Fire Extinguishers |  | Minimum 2 per floor. Depending up on the Area and Travel Distance
2 | Terrace Level Over Head Tank |  | 25000 Liters Capacity
3 | Under Ground Water Tank |  | Not required
4 | Terrace Fire Pump |  | 900 LPM
5 | Fire Pump near Under Ground Water Tank |  | Not required
6 | Hose Reel Assembly |  | Required
7 | Down Comes System |  | Required
8 | Wet Riser System |  | Not required
9 | Yard Hydrant |  | Not required
10 | Fire Service Inlet |  | Required
11 | Manually Operated Fire Alarm Call Point (MCP) |  | Required
12 | Automatic Detection and Alarm System |  | Not required
13 | Automatice Spinkler System |  | Required if area of basement exceeds 200 sq.mts
a | b |  | c
Life Safety (Passive Measures)
14 | Side Set Back Area |  | As per DCR and Local Body Rules
15 | Parking Faclity |  | Required
16 | Assembly Point |  | Required
17 | Compartmentation |  | Required
18 | Means of | Escape | Required
Exit Width
Travel Distance etc.,
19 | Staircases |  | 2 nos. required (Remote from each other not adjacent)
20 | Ramp |  | Not required
21 | Refuge Area |  | Not required
22 | Exit Signages |  | Required
23 | Sealing of Cable and other ducts at each floor level |  | Required
24 | Fire Damper at Air Conditioned Ducts |  | Required
25 | Fire Drill and Fire Order |  | Required
26 | Do's and Donts Laminated Hanging Pads |  | Required
27 | Lightning Arrester |  | Not required
28 | Smoke Ventilation System |  | Not required
29 | Training |  | Required
30 | House Keeping |  | Required
31 | Emergency Lights (at Staircase Landing and Exit Route) |  | Required
32 | Fire Lift |  | Required

## Group C
Requirement of the Fire Safety measures for Group C - Institutional Buildings – Above 15 m in height
Sl.No | Type of Fire Protection Required | C1- Hospitals, Sanatoria and Nursing Home |  | C2 - Custodial Institutions
C3 - Penal and Mental Institutions
| Fire Safety (Active Measures) | 15 Mts not exceeding | 24 Mts not exceeding | 15 Mts not exceeding | 24 Mts not exceeding
|  | 24 Mts | 30 Mts | 24 Mts | 30 Mts
a | b | c | d | e | f
1 | Fire Extinguishers | Minimum 2 per floor Depending upon the Area and Travel Distance
2 | Terrace Level Over Head Tank | 20,000 litres capacity | 20,000 litres capacity | 10,000 litres capacity | 20,000 litres capacity
3 | Under Ground Water Tank | 1.00,000 litres capacity | 1,50,000 litres capacity | 75,000 litres capacity | 1,00,000 litres capacity
4 | Terrace Fire Pump | Not required | Not Required | Not Required | Not Required
5 | Fire Pump near Under Group Water Tank | 1 electric pump & 1 Diesel pump of capacity 2280 LPM & Jockey Pump 180 LPM | 2 electric pump & 1 Diesel pump of capacity 2280 LPM & Jockey Pump 180 LPM | 1 electric pump & 1 Diesel pump of capacity 2280 LPM & Jockey Pump 180 LPM | 2 electric pump & 1 Diesel pump of capacity 2280 LPM & Jockey Pump 180 LPM
6 | Hose Reel Assembly | Required | Required | Required | Required
7 | Down Comer System | Not Required | Not Required | Not Required | Not Required
8 | Wet Riser System | Required | Required | Required | Required
9 | Yard Hydrant | Required | Required | Required | Required
10 | Fire Service Inlet | Required | Required | Required | Required
11 | Manually Operated Fire Alarm Call Point (MCP) | Required | Required | Required | Required
12 | Automatic Detection & Alarm System | Required | Required | Required | Required
13 | Automatic Sprinkler System | Required | Required | Required | Required
a | b | c | d | e | f
Life Safety (passive measure)
14 | Side Set Back Area | As per DCR and Local Body Rules
15 | Parking Facility | Required | Required | Required | Required
16 | Assembly Point | Required | Required | Required | Required
17 | Compartmentation | Required | Required | Required | Required
18 | Means of Escape | Required | Required | Required | Required
| Exit Width | 2 Mts | 2 Mts | 2 Mts | 2 Mts
| Travel Distance, etc | 30 Mts | 30 Mts | 30 Mts | 30 Mts
19 | Staircases | Required | Required | Required | Required
20 | Ramp | Required | Required | Required | Required
21 | Refuge Area | Required at every floor level
22 | Exit Signage’s | Required | Required | Required | Required
23 | Sealing of Cable and other ducts at each floor level | Required | Required | Required | Required
24 | Fire Damper at Air Conditioned Ducts | Required | Required | Required | Required
25 | Fire Drill and Fire Order | Required | Required | Required | Required
26 | Do’s and Don’ts Laminated Hanging Pads | Required | Required | Required | Required
27 | Lightning Arrester | Required | Required | Required | Required
28 | Smoke Ventilation System | Required | Required | Required | Required
29 | Training | Required | Required | Required | Required
30 | House Keeping | Required | Required | Required | Required
31 | Emergency Lights (at Staircase Landing and Exit Route | Required | Required | Required | Required
32 | Fire Lift | Required | Required | Required | Required
33 | Ambulance | Required | Required | Required | Required
34 | Separate toilet | Required specially designed for physically challenged patients | Required | Required | Required

## Group D
Requirement of the Fire Safety measures for Group D - Assembly Buildings Above 15 m in height
Sl.No | Type of Fire Protection Required | D1 - Theartre over 1000 persons, D2 upto 1000 persons D3 - Permanent Stage over 300 persons |  | D6 - Not exceeding 30 mtrs | D7 - Elevated or underground for assembly not covered D1-D6
D4 - upto 300 persons, D5 all others
| Fire Safety (Active Measures) | 15 Mts not exceeding | 24 Mts not exceeding | 15 Mts not exceeding | 24 Mts not exceeding
|  | 24 Mts | 30 Mts | 24 Mts | 30 Mts
a | b | c | d | e | f
1 | Fire Extinguishers | Minimum 2 per floor Depending upon the Area and Travel Distance
2 | Terrace Level Over Head Tank | 10,000 litres capacity | 20,000 litres capacity | 20,000 litres capacity | 20,000 litres capacity
3 | Under Ground Water Tank | 75,000 litres capacity | 1,00,000 litres capacity | 1,00,000 litres capacity | 1,00,000 litres capacity
D1-D5, 2,00,000 litres for D6 Multiplex
4 | Terrace Fire Pump | Not required | Not Required | Not Required | Not Required
5 | Fire Pump near Under Group Water Tank | 1 electric pump & 1 Diesel pump of capacity 2280 LPM & Jockey Pump 180 LPM | 2 electric pump & 1 Diesel pump of capacity 2280 LPM & Jockey Pump 180 LPM | 2 electric pump & 1 Diesel pump of capacity 2850 LPM & Jockey Pump 180 LPM | 2 electric pump & 1 Diesel pump of capacity 2850 LPM & Jockey Pump 180 LPM
6 | Hose Reel Assembly | Required | Required | Required | Required
7 | Down Comer System | Not Required | Not Required | Not Required | Not Required
8 | Wet Riser System | Required | Required | Required | Required
9 | Yard Hydrant | Required | Required | Required | Required
10 | Fire Service Inlet | Required | Required | Required | Required
11 | Manually Operated Fire Alarm Call Point (MCP) | Required | Required | Required | Required
12 | Automatic Detection & Alarm System | Required | Required | Required | Required
13 | Automatic Sprinkler System | Required | Required | Required | Required
a | b | c | d | e | f
Life Safety (passive measure)
14 | Side Set Back Area | As per DCR and Local Body Rules | As per DCR and Local Body Rules | As per DCR and Local Body Rules | As per DCR and Local Body Rules
15 | Parking Facility | Required | Required | Required | Required
16 | Assembly Point | Required | Required | Required | Required
17 | Compartmentation | Required | Required | Required | Required
18 | Means of Escape | Required | Required | Required | Required
| Exit with | 2 Mts | 2 Mts | 2 Mts | 2 Mts
| Travel Distance , etc | 30 Mts | 30 Mts | 30 Mts | 30 Mts
19 | Staircases | Required | Required | Required | Required
20 | Ramp | Required If basement floor | Required If basement floor | Required If basement floor | Required If basement floor
21 | Refuge Area | Not Required | Required at 24th mtrs level | Required at 24th mtrs level | Required at 24th mtrs level
22 | Exit Signage’s | Required | Required | Required | Required
23 | Sealing of Cable and other ducts at each floor level | Required | Required | Required | Required
24 | Fire Damper at Air Conditioned Ducts | Required | Required | Required | Required
25 | Fire Drill and Fire Order | Required | Required | Required | Required
26 | Do’s and Don’ts Laminated Hanging Pads | Required | Required | Required | Required
27 | Lightning Arrester | Required | Required | Required | Required
28 | Smoke Ventilation System | Required | Required | Required | Required
29 | Training | Required | Required | Required | Required
30 | House Keeping | Required | Required | Required | Required
31 | Emergency Lights (at Staircase Landing and Exit Route | Required | Required | Required | Required
32 | Fire Lift | Required | Required | Required | Required

## Group E
Requirement of the Fire Safety measures for Group E - Business Buildings Above 15 m in height
Sl.No | Type of Fire Protection Required | E1 offices, banks, professional establishments, like offices of architects, engineers, doctors, lawyers and police stations, E2 - Laboratories research establishments, libraries and test houses. E3 - Computer installations, E4 - Telephone Exchanges, E5
| Fire Safety (Active Measures) | 15 Mts not exceeding 24 Mts | 24 Mts not exceeding 30 Mts | Above 30 mtr
a | b | c | d | e
1 | Fire Extinguishers | Minimum 2 per floor Depending upon the Area and Travel Distance | Minimum 2 per floor Depending upon the Area and Travel Distance | Minimum 2 per floor Depending upon the Area and Travel Distance
2 | Terrace Level Over Head Tank | 10,000 litres capacity | 20,000 litres capacity | 20,000 litres capacity
3 | Under Ground Water Tank | 75,000 litres capacity | 1,00,000 litres capacity | 2,00,000 litres capacity
4 | Terrace Fire Pump | Not required | Not Required | Not Required
5 | Fire Pump near Under Group Water Tank | 1 electric pump & 1 Diesel pump of capacity 2280 LPM & Jockey Pump 180 LPM | 2 electric pump & 1 Diesel pump of capacity 2280 LPM & Jockey Pump 180 LPM | 2 electric pump & 1 Diesel pump of capacity 2850 LPM & Jockey Pump 180 LPM
6 | Hose Reel Assembly | Required | Required | Required
7 | Down Comer System | Not Required | Not Required | Not Required
8 | Wet Riser System | Required | Required | Required
9 | Yard Hydrant | Required | Required | Required
10 | Fire Service Inlet | Required | Required | Required
11 | Manually Operated Fire Alarm Call Point (MCP) | Required | Required | Required
12 | Automatic Detection & Alarm System | Required | Required | Required
13 | Automatic Sprinkler System | Required | Required | Required
a | b | c | d | e
Life Safety (passive measure)
14 | Side Set Back Area | As per DCR and Local Body Rules
15 | Parking Facility | Required | Required | Required
16 | Assembly Point | Required | Required | Required
17 | Compartmentation | Required | Required | Required
18 | Means of Escape | Required | Required | Required
| Exit width | 2 Mts | 2 Mts | 2 Mts
| Travel Distance, etc | 30 Mts | 30 Mts | 30 Mts
19 | Staircases | Required | Required | Required
20 | Ramp | Required If basement floor | Required If basement floor | Required If basement floor
21 | Refuge Area | Not Required | Required at 24th mtrs level | Required at 24th mtrs level and every 15 mtrs level one.
22 | Exit Signage’s | Required | Required | Required
23 | Sealing of Cable and other ducts at each floor level | Required | Required | Required
24 | Fire Damper at Air Conditioned Ducts | Required | Required | Required
25 | Fire Drill and Fire Order | Required | Required | Required
26 | Do’s and Don’ts Laminated Hanging Pads | Required | Required | Required
27 | Lighting Arrester | Required | Required | Required
28 | Smoke Ventilation System | Required | Required | Required
29 | Training | Required | Required | Required
30 | House Keeping | Required | Required | Required
31 | Emergency Lights (at Staircase Landing and Exit Route | Required | Required | Required
32 | Fire Lift | Required | Required | Required

## Group F
Requirement of the Fire Safety measures for Group F Mercantile Building Above 15 m in height
Sl.No | Type of Fire Protection Required | F1 - Shops, Stores upto 500 Sq.m, |  | F3 - Under ground shopping centre and Storage
F2 - Shops, Stores more than 500 Sq.mtrs.
| Fire Safety (Active Measures) | 15 Mts not exceeding 24 Mts | 24 Mts not exceeding 30 Mts
a | b | c | d | e
1 | Fire Extinguishers | Minimum 2 per floor Depending upon the Area and Travel Distance
2 | Terrace Level Over Head Tank | 10,000 litres capacity | 10,000 litres capacity | 10,000 litres capacity
3 | Under Ground Water Tank | 1,00,000 litres capacity | 1,50,000 litres capacity | 1,50,000 litres capacity
4 | Terrace Fire Pump | Not required | Not Required | Not Required
5 | Fire Pump near Under Group Water Tank | 1 electric pump & 1 Diesel pump of capacity 2280 LPM & Jockey Pump 180 LPM | 2 electric pump & 1 Diesel pump of capacity 2280 LPM & Jockey Pump 180 LPM | 2 electric pump & 1 Diesel pump of capacity 2280 LPM & Jockey Pump 180 LPM
6 | Hose Reel Assembly | Required | Required | Required
7 | Down Comer System | Not Required | Not Required | Not Required
8 | Wet Riser System | Required | Required | Required
9 | Yard Hydrant | Required | Required | Required
10 | Fire Service Inlet | Required | Required | Required
11 | Manually Operated Fire Alarm Call Point (MCP) | Required | Required | Required
12 | Automatic Detection & Alarm System | Required | Required | Required
13 | Automatic Sprinkler System | Required | Required | Required
a | b | c | d | e
Life Safety (passive measure)
14 | Side Set Back Area | As per DCR and Local Body Rules
15 | Parking Facility | Required | Required | Required
16 | Assembly Point | Required | Required | Required
17 | Compartmentation | Required | Required | Required
18 | Means of Escape | Required | Required | Required
| Exit Width | 1.5 Mts | 1.5Mts | 1.5 Mts
| Travel Distance, etc | 30 Mts | 30 Mts | 30 Mts
19 | Staircases | Required | Required | Required
20 | Ramp | Required If basement floor | Required If basement floor | Required If basement floor
21 | Refuge Area | Not Required | Required at 24th mtrs level | Not Required
22 | Exit Signage’s | Required | Required | Required
23 | Sealing of Cable and other ducts at each floor level | Required | Required | Required
24 | Fire Damper at Air Conditioned Ducts | Required | Required | Required
25 | Fire Drill and Fire Order | Required | Required | Required
26 | Do’s and Don’ts Laminated Hanging Pads | Required | Required | Required
27 | Lighting Arrester | Required | Required | Required
28 | Smoke Ventilation System | Required | Required | Required
29 | Training | Required | Required | Required
30 | House Keeping | Required | Required | Required
31 | Emergency Lights (at Staircase Landing and Exit Route | Required | Required | Required
32 | Fire Lift | Required | Required | Required

## Group G
Requirement of the Fire Safety measures for Group G Industrial Buildings Above 15 m in height not to be permitted 18 Mts in height
Sl. No | Type of Fire Protection Required | G1 - Low Hazard Industries |  |  | G2 - Moderate Hazard Industries
BUILT UP AREA
| Fire Safety (Active Measures) | upto 100 Sq.mt | More than 100 Sq.mt. & upto 500 Sq.mt | More than 500 Sq.mtrs | Upto 100Sq.mtrs | More than 100Sq.mtrs and upto 500 Sq.mtrs |  | More than 500Sq.mtrs and upto 1000 Sq.mtrs | Upto 1000 Sq.mt
a | b | c | d | e | f | g | h |  | i
1 | Fire Extinguishers | Minimum 2 per floor Depending upon the Area and Travel Distance
2 | Terrace Level Over Head Tank | 5000 litres in case of basement area exceeds 200m2 | 5000 litres add 5000 litres if the provision of sprinkler in basement | 10,000 litres capacity | 10,000 Liters capacity | 10,000 Liters capacity | 20,000 Litres capacity |  | 20,000 Litres capacity
3 | Under Ground Water Tank | Not required | Not required | 1,00,000 litres | Not required | Not required | 75,000 Litres capacity |  | 1,00,000 Litres capacity
4 | Terrace Fire Pump | 450 LPM | 450 LPM | 450 LPM | 900 LPM | 900 LPM | 900 LPM |  | 900 LPM
5 | Fire Pump near Under Group Water Tank | Not required | Not required | 1 electric pump & 1 Diesel pump of capacity 2280 LPM & Jockey Pump 180 LPM | Not required | Not required | 1 electric pump & 1 Diesel pump of capacity 2280 LPM & Jockey Pump 180 LPM |  | 1 electric pump & 1 Diesel pump of capacity 2280 LPM & Jockey Pump 180 LPM
6 | Hose Reel Assembly | Not required | Required | Required | Required | Required | Required |  | Required
7 | Down Comer System | Not required | Required | Required | Not required | Not required | Required |  | Required
8 | Wet Riser System | Not required | Not required | Required | Not Required | Not Required | Required |  | Required
9 | Yard Hydrant | Not required | Not required | Required | Not Required | Not Required | Required |  | Required
10 | Fire Service Inlet | Not required | Not required | Required | Not Required | Not Required | Required |  | Required
11 | Manually Operated Fire Alarm Call Point (MCP) | Not required | Not required | Not Required | Not Required | Not Required | Required |  | Required
12 | Automatic Detection & Alarm System | Not required | Not required | Required | Not Required | Not Required | Required |  | Required
13 | Automatic Sprinkler System | Required (if there is basement) | Required (if there is basement) | Required | Required | Required | Required |  | Required
Life Safety (passive measure)
14 | Side Set Back Area | As per DCR and Local Body Rules
15 | Parking Facility | Required | Required | Required | Required | Required | Required |  | Required
16 | Assembly Point | Required | Required | Required | Required | Required | Required |  | Required
17 | Compartmentation | Required | Required | Required | Required | Required | Required |  | Required
18 | Means of Escape | Required | Required | Required | Required | Required | Required |  | Required
| Exit Width | 1.5 Mtrs | 1.5 Mtrs | 1.5 Mtrs | 1.5 Mtrs | 1.5 Mtrs | 1.5 Mtrs |  | 1.5 Mtrs
| Travel Distance etc. | 45 Mtrs | 45 Mtrs | 45 Mtrs | 45 Mtrs | 45 Mtrs | 45 Mtrs |  | 45 Mtrs
19 | Staircases | Required | Required | Required | Required | Required | Required |  | Required
20 | Ramp | Not required | Not required | Not required | Not required | Not required | Not required |  | Not required
21 | Refuge Area | Not required | Not required | Not required | Not required | Not required | Not required |  | Not required
22 | Exit Signage’s | Required | Required | Required | Required | Required | Required |  | Required
23 | Sealing of Cable and other ducts at each floor level | Required | Required | Required | Required | Required | Required |  | Required
24 | Fire Damper at Air Conditioned Ducts | Required | Required | Required | Required | Required | Required |  | Required
25 | Fire Drill and Fire Order | Required | Required | Required | Required | Required | Required |  | Required
26 | Do’s and Don’ts Laminated Hanging Pads | Required | Required | Required | Required | Required | Required |  | Required
27 | Lighting Arrester | Required | Required | Required | Required | Required | Required |  | Required
28 | Smoke Ventilation System | Required | Required | Required | Required | Required | Required |  | Required
29 | Training | Required | Required | Required | Required | Required | Required |  | Required
30 | House Keeping | Required | Required | Required | Required | Required | Required |  | Required
31 | Emergency Lights (at Staircase Landing and Exit Route | Required | Required | Required | Required | Required | Required |  | Required